## Φύλλο1
ΠΙΝΑΚΑΣ ΑΝΤΑΛΛΑΚΤΙΚΩΝ
Remark : According to the provisions (desrciptions and notes) of Annex 4 of Project Outline (B0)
Item | DESCRIPTION | Quantity per engine cylinder | Total number of pieces / sets | Price (Euro)
No
MECHANICAL SPARE PARTS
Part A: Engines' Spare Parts
I. CYLINDER HEAD
1 | Cylinder head complete assembled with fuel and air valves (1) | 0,02 set | * sets
2 | Joints for cylinder head and liner complete (1) | 0,04 set | * sets
3 | Complete set of cylinder head joints and O-rings (1) | 0,04 set | * sets
4 | Starting air valve complete (1) | 0,03 pc | * pcs
5 | Indicator valve complete (1) | 0,03 pc | * pcs
6 | Flexible hoses for fuel, oil, cooling water, etc(1) | 0,03 pc | * pcs
II. INLET AND EXHAUST VALVES
7 | Exhaust valve assembly complete (with cage and valve) (1) | 0,075 pc | * pcs
8 | Exhaust valve seat or exhaust valve cage (1) | 0,075 pc | * pcs
9 | Exhaust valve bare | 0,075 pc | * pcs
10 | Springs set complete (all springs for exhaust valve) | 0,075 set | * sets
11 | Gaskets and rings of all types for exhaust valve (1) | 0,075 set | * sets
12 | Exhaust valve guide | 0,075 pc | * pcs
13 | Rotocap | 0,075 pc | * pcs
14 | Intake valve complete (1) | 0,075 pc | * pcs
15 | Intake valve seat or bottom of cage | 0,075 pc | * pcs
16 | Intake valve bare | 0,075 pc | * pcs
17 | Springs set complete (all springs for intake valve) | 0,075 set | * sets
18 | Intake valve guide | 0,075 pc | * pcs
19 | Rocker arm (all kinds) (1) | 0,075 set | * pcs
20 | Intake valve cam (part or camshaft) | 0,05 pc | * pcs
21 | Outlet valve cam (part or camshaft) | 0,05 pc | * pcs
III. CHARGE AIR / EXHAUST GAS SYSTEM
22 | Charge air inlet sleeve | 0,1 pc | * pcs
23 | Turbocharger complete | 1 set per 10 UNITS but not less than 1
| Turbocharger pilot valve/positioner | 2 pcs per 10 UNITS but not less than 2
| Turbocharger bypass valve | 1 pc per 10 UNITS but not less than 1
24 | Charge air cooler of each type and size complete(1) | 1 pc per 10 UNITS but not less than 1
25 | Expansion bellows for exhaust piping (all kinds installed) (1) | 2 pcs per 10 UNITS but not less than 2
IV. FUEL SYSTEM
26 | Gas valve for main combustion chamber, complete | 1 pc per 6 UNITS
27 | Gas valve for pre-combustion chamber, complete | 1 pc per 6 UNITS
28 | Bidder shall provide all recommended spare parts for 2 years operation of each UNIT’s fuel system, including of each Gas Valve Unit. For this list of recommended spare parts, Bidder shall give a detailed analysis with the respective unit prices. (1) | 1 set per UNIT
V. IGNITION SYSTEM
29 | Spark plug | 1 pc | * pcs
VI. CYLINDER PISTON
30 | Piston complete assembled (crown, skirt, connecting rod, etc) (1) | 0,015 pc | * pcs
31 | Piston crown | 0,025 pc | * pcs
32 | Piston skirt | 0,025 pc | * pcs
33 | Piston connecting bolts (set with locking plate or spring complete (1)) | 0,04 set | * sets
34 | Complete set of piston rings (1) | 0,15 set | * sets
35 | Gudgeon pin cover | 0,04 pc | * pcs
36 | Locking plate (or spring) for gudgeon pin cover | 0,04 pc | * pcs
37 | Piston gudgeon pin | 0,04 pc | * pcs
VII. CONNECTING ROD
38 | Connecting rod complete (1) | 1 pc per 10 UNITS but not less than 1
39 | Connecting rod small end bearing (1) | 0,04 pc | * pcs
40 | Connecting rod big end bearing (1) | 0,04 pc | * pcs
41 | Complete set of bolts and nuts for big end of connecting rod with locking plate or spring complete (1) | 0,04 sets | * sets
VIII. LINER
42 | Liner complete(1) | 0,02 pc | * pcs
43 | Water jacket complete (1) | 1 pc per 10 UNITS but not less than 1
44 | Complete set of sealing O-rings of the liner (1) | 0,02 pc | * sets
IX. CAMSHAFT
45 | Camshaft bearings of each type and size | 1 set per 10 UNITS but not less than 1
X. FRAME-CRANKSHAFT
46 | Tie rod complete with nuts and cover | 0,04 pc | * pcs
47 | Crankshaft main bearing upper and lower shell complete (1) | 2 pcs per 10 UNITS but not less than 2
48 | Complete set of timing system driven gears (1) | 1 set per 10 UNITS but not less than 1
49 | Crankshaft thrust bearing | 1 pc per 10 UNITS but not less than 1
XI. FILTERS
50 | Fuel gas filter cartridges complete set for each filter if applicable (1) | 1 set per UNIT
51 | Lube oil and pre lube oil filter cartridges complete set for each filter (1) | 1 set per UNIT
52 | Sealing rings, o-rings, gaskets for each filter complete (1) | 1 set per UNIT
Part B: Spare Parts for Engines' Auxiliary Systems and Project Rest Equipment
1 | STARTING AIR SYSTEM
1.1 | Air compressors
| Wear and sealing parts(1) |  | 2 sets
| Standard service kit for two years operation(1) |  | 1 set
1.2 | Oil and water separators
| Standard service kit for two years operation(1) |  | 1 set
1.3 | After coolers
| Standard service kit for two years operation(1) |  | 1 set
1.4 | Filters
| Final filter cartridge, per UNIT offered |  | 1 pc
1.5 | Other equipment of the starting air system
| Repair kit for each automatic drain valve(1) |  | 1 set
2 | FUEL GAS SYSTEM
2.1 | Complete valves, 10% of each type and size installed but at least one of each (including actuator) |  | 1 set
2.2 | Diaphragm for each type and size of valve |  | 2 pcs
2.3 | Gaskets and packings for each type and size of valves |  | 2 sets
2.4 | Complete natural gas compressor rotor with bearings and coupling (if applicable) |  | 1 set
2.5 | 10% of any type of gas detectors complete with base, but not less than 2 pcs per type |  | 1 set
2.6 | Bidder shall specify all other recommended spare parts for two years of operation of the system, including among others of the gas-fired water heaters, of the gas leakage detection system and of the nitrogen station(s) (1) |  | 1 set
3 | LUBE OIL SYSTEMS
3.1 | Lube oil circulating pump complete |  | 1 pc
3.2 | For each other pump of the lube oil systems
| Complete shaft with impeller, bearings and whole coupling |  | 1 pc
| One set wearing rings and sealing parts(1) |  | 1 set
3.3 | One cartridge for each filter of the lube oil systems |  | 1 set
3.4 | Lube oil centrifugal separators
| Bidder shall provide all recommended spare parts for 2 years operation of each lube oil centrifugal separator(1) |  | 1 set per UNIT
4 | COOLING SYSTEM
4.1 | Coolers (heat-exchangers)
| Shell & tube type: 5% of total number of tubes installed, for each type installed |  | 1 set
| Plate type: 5% of the total plates and 10% of the total gaskets installed, for each type installed |  | 1 set
4.2 | Cooling water circulating pumps
4.2.1 | For each type of pump installed: Complete rotor with impeller, bearings and the whole coupling |  | 1 set per 5 UNITS
4.2.2 | Repair kit including gaskets, wearing rings, packings and sealing parts(1) |  | 1 set per 5 UNITS
5 | DISTRICT HEATING PRODUCTION SYSTEM (DHPS)
5.1. | Heat-exchangers
| Shell & tube type: 5% of total number of tubes installed, for each type installed |  | 1 set
| Plate type: 5% of the total plates and 10% of the total gaskets installed, for each type installed |  | 1 set
5.2 | Closed Water Circuit Pumps
| For each type of pump installed: Complete rotor with impeller, bearings and the whole coupling |  | 1 set per 3 UNITS
| Repair kit including gaskets, wearing rings, packings and sealing parts(1) |  | 1 set per 3 UNITS
5.3 | Dampers
| Set of shaft of the flue gas damper |  | 1 set per 4 UNITS
| Set of louvers/blade of the flue gas damper |  | 1 set per 4 UNITS
6 | LIFTING EQUIPMENT
6.1 | Complete sets of bearings of each type and size installed |  | 2 sets
6.2 | Set of spare parts for the brakes of each type and size installed(1) |  | 2 sets
6.3 | Set of brake operating devices of each type and size installed(1) |  | 2 sets
6.4 | Set of limit switches of each type and size installed |  | 2 sets
6.5 | Set of ropes, chains, guides of each type and size installed |  | 2 sets
6.6 | Set of all other required components subjected to wear and tear(1) |  | 2 sets
7 | COMPRESSED AIR SYSTEM
7.1 | Bidder shall specify all recommended spare parts for two years of operation of the system, incl. of the compressors, filters, dryers and valves (including actuators, if any). (1) |  | 1 set
8 | HVAC SYSTEMS
8.1 | Spare filter for each type and size installed |  | 2 pcs
8.2 | Spare belt for each type and size installed (if applicable) |  | 1 pc
8.3 | Safety valve for each type and size installed (complete) |  | 1 pc
8.4 | Complete damper (with actuator) for each type and size installed |  | 1 pc
8.5 | Compressors of chillers
| Standard service kit for each type and size installed(1) |  | 1 set
8.6 | Bidder shall specify various spare parts for all other HVAC equipment (AHUs, FCUs, etc) for 2 years operation. (1) |  | 1 set
9 | FIRE FIGHTING SYSTEMS
9.1 | 10% of each type and size of fire fighting hoses, but not less than 2 pcs per type |  | 1 set
9.2 | 10% of internal equipment and special tools for each type and size of indoor and outdoor hydrant, but for not less than 2 indoor and 2 outdoor hydrants(1) |  | 1 set
9.3 | 10% of each type and size of nozzles/sprinklers installed, but not less than 2 pcs per type |  | 1 set
9.4 | Bidder shall specify various spare parts for all other fire-fighting equipment (deluge, fixed CO2, fixed/portable foam, etc) for 2 years operation. (1) |  | 1 set
10 | VARIOUS VALVES (including steam traps)
(not mentioned elsewhere)
10.1 | For each type, size and rating of valves greater than DN 50, complete repair kit (including internals, seats, packings, gaskets, seals, parts for actuator if applicable, etc.) (1) |  | 2 sets
10.2 | For each type, size and rating of valves installed, up to DN 50, one complete valve including actuator (if applicable) |  | 1 set
10.3 | For each valve, not mentioned elsewhere, of the following types, per nominal bore and nominal rating installed
| pilot valves |  | 1 complete
| solenoid valves |  | 1 complete
| diaphragm valves |  | 1 complete
| internal pieces for pilot valves(1) |  | 1 set
| internal pieces for solenoid valves(1) |  | 1 set
| internal pieces for diaphragm valves(1) |  | 1 set
10.4 | For each size and rating of safety valves installed, complete repair kit (1) |  | 2 sets
11 | VARIOUS GASKETS (not mentioned elsewhere)
11.1 | For each type and kind of gaskets installed |  | 2 sets
12 | VARIOUS PUMPS (not mentioned elsewhere)
For each type and size of installed pumps of the PROJECT not mentioned elsewhere
12.1 | Complete rotor with impeller/gears, bearings and the whole coupling |  | 1 set
12.2 | Repair kit including gaskets, wearing rings, packings and sealing parts(1) |  | 1 set
13 | VARIOUS HEAT EXCHANGERS (not mentioned elsewhere)
13.1 | 5% of total number of tubes installed, for each type installed (or 5% of the total plates installed, for each type installed in plate heat exchangers). |  | 1 set
14 | PIPING & DUCTS
14.1 | Bidder shall specify various spare parts for all piping/ducts (including piping/ducts, fittings, expansion joints, hangers, supports, anchors, etc) for 2 years operation, but not less than 5% of installed quantities for all kinds of piping/duct material, quality and dimensions. (1) |  | 1 set
15 | VARIOUS FANS (not mentioned elsewhere)
15.1 | For each type and size of installed fans:
| - set of bearings |  | 2 sets
| - set of belts (if applicable) |  | 2 sets
16 | VARIOUS DAMPERS (not mentioned elsewhere)
16.1 | For each type and size, one set of shaft of the damper |  | 1 set
16.2 | For each type and size, one set of louvers/blade of the damper |  | 1 set
17 | MISCELLANEOUS
17.1 | Bidder shall specify all other recommended spare parts of the rest mechanical systems of the PROJECT necessary for 2 years of operation(1) |  | 1 set
TOTAL PRICE FOR THE MECHANICAL SPARE PARTS
ELECTRICAL SPARE PARTS
1 | GENERATORS
1.1 | Set of bearings comprising one at the DE and one at the NDE of the Gas Engine Generators (2 pieces in total) |  | 1 set
1.2 | Set (the total number installed in one Generator) of brushholders and brushholder fixation bars of all types mounted on the Gas Engine Generators |  | 1 set
1.3 | Set (the total number installed in one Generator) of brushes of all types of the Gas Engine Generators |  | 1 set
1.4 | Set of bushings comprising 1pc for HV side and 1pc for neutral side of the Gas Engine Generators |  | 1 set
1.5 | One complete air to water or air to air heat exchanger of the Gas Engine Generators (if any) |  | 1 pc
1.6 | Neutral transformer load resistors, one per type for Gas Engine Generators |  | 1 set
1.7 | One of each type of current transformers installed at the neutral side for the Gas Engine Generators |  | 2 sets
2. | AUTOMATIC VOLTAGE REGULATORS
2.1 | 20%, but not less than two, complete printed circuit boards (p.c.b.) for each type of p.c.b. installed in the A.V.R. of the Gas Engine Generators |  | 1 set
2.2 | 20%, but not less than two pieces of each type of communication boards and switches installed for serial communication of the Power Plant with the Gas Engine Generators |  | 1 set
2.3 | 10%, but not less than two pieces, for each type of power supply units and power distribution modules installed for the Gas Engine Generators |  | 1 set
3. | EXCITATION SYSTEM
3.1 | Complete set (the total number installed in one Generator) of thyristors, including the relevant RC circuits, per each type installed for the Gas Engine Generators |  | 1 set
3.2 | Complete set (the total number installed in one Generator) of fuses for thyristors, per each type installed for the Gas Engine Generators |  | 2 sets
3.3 | Set of spares for field suppression including resistors, de-excitation thyristor, or contactor, or CROW-BAR of each type installed for the Gas Engine Generators |  | 1 set
3.4 | 20%, but not less than two, complete printed circuit boards (p.c.b.) and modules for each type installed e.g. for thyristors driving, thyristors conduction monitoring, input/output signaling, excitation protections, rotor protections, field suppression, field flashing, etc. for the Gas Engine Generators |  | 1 set
3.5 | Set of complete bridge of rotating diodes (the total number installed in one Generator) for the Gas Generators |  | 1 set
3.6 | Set of diodes, resistors, capacitors, varistors (two pieces of each type installed in one Generator) |  | 1 set
4. | GENERATOR (STEP-UP) TRANSFORMER
4.1 | Complete HV bushing |  | 2 pc
4.2 | Complete LV bushing |  | 2 pc
4.3 | Complete neutral bushing |  | 1 pc
4.4 | Complete air blower with motor |  | 1 set
4.5 | Complete set of gaskets |  | 1 set
4.6 | Winding temperature monitoring relay |  | 1 pc
4.7 | Buchholz relay |  | 1 pc
4.8 | Winding temperature indicator |  | 1 pc
4.9 | Oil temperature indicator |  | 1 pc
4.10 | Oil level indicator |  | 1 pc
4.11 | Quick pressure rise protection relay |  | 1 pc
4.13 | Pressure relief valve |  | 1 pc
4.14 | One of each type of oil temperature sensors installed |  | 1 set
4.15 | One of each type of current transformers installed |  | 1 set
4.16 | One of each type of silica-gel breather installed |  | 1 set
4.17 | One of each type of HV side surge arresters installed |  | 2 sets
4.18 | One of each type of winding and oil temperature transmitters installed |  | 1 set
5. | STATION SERVICE TRANSFORMERS
5.1 | One complete transformer per each rating installed including casing |  | 1 set
5.2 | One complete isolating transformer (400/400V) per each rating installed including casing |  | 1 set
5.3 | One of each type of temperature monitoring device installed |  | 1 set
5.4 | One piece of each type of lightning arresters installed (if not installed at the MV switchgear) |  | 2 sets
6. | 10÷15 kV SWITCHGEAR
6.1 | One of each type and rating of complete circuit breaker installed |  | 1 set
6.2 | One of each type of lightning arresters installed |  | 2 sets
6.3 | One of each type of voltage and current transformers including toroidal transformers installed |  | 1 set
6.4 | Set of closing and tripping coils, aux. relays including, varistors and diodes, spring charging motor, aux. contacts, truck blocking magnet, undervoltage release, etc. for each type of breakers or contactor installed (two of each type) |  | 2 sets
6.5 | Set of arc detection devices. Each set shall consist of: |  | 1 set
- three sensors of each type installed
- one monitor unit of each type installed
- one sensor glass cord per each length installed
6.7 | 5% of each type of auxiliaries relays with bases, varistors and diodes installed in the low voltage compartments and not less than two per type |  | 1 set
6.8 | 5% of each type of fuses installed in the low voltage compartments and not less than two per type |  | 1 set
6.9 | One of each type of voltage monitoring relays installed in the low voltage compartments |  | 1 set
6.10 | 5% of each type of push buttons, indicating lamps and leds including lamp holders and capacitor dividers with lamps installed in the low voltage compartments and not less than two per type |  | 1 set
6.11 | One of each type of indicating ammeters and voltmeters installed |  | 1 set
6.12 | One of each type of current and voltage transmitters installed |  | 1 set
6.13 | One of each type of feeder earthing switch including locking magnet installed |  | 1 set
6.14 | Complete set (the total number installed) of fuses at HV side type of VTs |  | 1 set
6.15 | One of each type of protection relays test sockets installed |  | 1 set
6.16 | One of each type of power supply units, DC/DC converters and suppression filters installed |  | 1 set
6.17 | Set of power and control plugs and sockets (including sliding contacts), as well as all mechanical interlocks, for each type of draw-out circuit breaker installed |  | 1 set
6.18 | Special grease for greasing all power contacts of draw-out breakers and VTs (plugs and sockets), as well as all mechanical interlocking mechanisms |  | 2 kg
7. | LV DISTRIBUTIONS, SUBDISTRIBUTIONS AND LOCAL BOARDS (i.e. 400 V AC, 220 V DC, 24V DC)
7.1 | One air circuit breaker (ACB) complete per each type installed |  | 1 set
7.2 | 5% of each type of moulded case circuit breakers (MCCB) installed and not less than one per type |  | 1 set
7.3 | 5% of each type of miniature circuit breakers (MCB) installed and not less than two per type |  | 1 set
7.4 | One complete drawer of each type installed. The type is defined according to the size of drawer, the wiring diagram, as well as the type of all components, including fuse holder and fuse links |  | 1 set
7.5 | Set of arc detection devices. Each set shall consist of: |  | 1 set
- three sensors of each type installed
- one monitor unit of each type installed
- one sensor glass cord per each length installed
7.6 | 5% of each type of contactors installed and not less than two per type |  | 1 set
7.7 | 5% of each type of thermal overload relays installed and not less than two per type |  | 1 set
7.8 | 5% of each type of fuses installed and not less than three per type |  | 1 set
7.9 | 5% of each type of load switches installed and not less than one per type |  | 1 set
7.10 | 5% of each type of auxiliary relays with bases, varistors and diodes installed and not less than two per type |  | 1 set
7.11 | Three of each type of surge arresters installed |  | 1 set
7.12 | One of each type of voltage monitoring relays installed |  | 1 set
7.13 | 5% of each type of installed push buttons, indicating LEDs and lamps, including lamp holders and not less than two per type |  | 1 set
7.14 | One of each type of power supply units, step-down transformers and isolating transformers installed at the local boards |  | 1 set
7.15 | One of each type of indicating ammeters and voltmeters installed |  | 1 set
7.16 | One of each type of synchronization monitoring devices installed |  | 1 set
7.17 | One of each type of voltage and current transformers and DC shunts installed including the ones integrated in circuit breakers with electronic trip units |  | 1 set
7.18 | One of each type of current, voltage and frequency transmitters installed |  | 1 set
7.19 | One of each type of earth fault monitoring relays and residual current monitoring relays installed |  | 1 set
7.20 | One of each type of residual voltage monitoring relays installed |  | 1 set
7.21 | One of each type of insulation monitoring relays installed for DC switchgear and secured AC switchgear |  | 1 set
7.22 | One of each type of thermistor monitoring relays installed for open loop actuators |  | 1 set
7.23 | One of each type of fuse monitoring relays installed |  | 1 set
7.24 | 5% of each type of decoupling diodes installed and not less than two per type |  | 1 set
7.25 | Set of power and control plugs and sockets (including sliding contacts), as well as all mechanical interlocks, for each type of draw-out circuit breaker installed (two per each type installed) |  | 1 set
7.26 | Set of auxiliary contacts, closing and tripping coils, spring charging motor etc. for each type of circuit breaker installed (two per each type installed) |  | 1 set
7.27 | Set of power and control plugs and sockets, as well as all mechanical interlocks, for each type of drawer installed |  | 1 set
7.28 | Electronic trip unit of circuit breaker, per each type installed |  | 1 set
7.29 | Special grease for greasing all power contacts of draw-out breakers (plugs and sockets), as well as all mechanical interlocking mechanisms |  | 2 kg
8. | BATTERIES
8.1 | 5% of the cells of all the 220V DC batteries installed, delivered in "dry condition" |  | 1 set
8.2 | 5% of the cells of any other batteries installed |  | 1 set
8.3 | Complete set (the total number installed) of fuses at fuse boxes |  | 1 set
9. | 220 V DC, AND ANY OTHER DC BATTERY CHARGERS, DC/AC INVERTERS, AND DC/DC CONVERTER
9.1 | One complete charger, one complete DC/AC inverter, and one complete DC/DC converter of each type, voltage level and rating installed all over the Power Plant. |  | 1 set
10. | EMERGENCY DIESEL GENERATOR SET
10.1 | Complete set suitable for, at least, 3000 hours of running i.e. spare parts for cylinder head, rod and piston, injector, camshaft, water pump, filters, generator, electrical equipment etc. |  | 1 set
10.2 | One man-machine interface device equipped with keyboard and LCD display |  | 1 pc
10.3 | EDG circuit breaker |  | 1 pc
10.4 | One of each type of voltage and current transformers installed |  | 1 set
10.5 | One complete printed circuit board (p.c.b.) and module for each type installed e.g. for speed and voltage regulation, input/output signaling, excitation, etc. |  | 1 set
10.6 | One of each type of auxiliary relays and under voltage relays installed |  | 1 set
10.7 | One of each type of fuses and contactors installed |  | 1 set
10.8 | One of each type of heaters and thermostats installed |  | 1 set
10.9 | Complete rotating diodes assembly |  | 1 set
10.10 | Set of generator drive end and non-drive end bearings |  | 1 set
11. | MOTORS AND ACTUATORS
11.1 | Motors > 10 kW
| - Bearings |  | 1 set per motor type and rating
| - Heaters |  | 1 set per motor type and rating
| - Bearing vibration sensors (if any) |  | 1 set per motor type and rating
11.2 | Complete motor for each type and rating of the LV motors, which have no installed 100% redundancy |  | 1 set
11.3 | One actuator for each type and rating of open loop actuators installed (actuator is meant complete i.e. comprising motor, reduction gear, stroke mechanism, integral control unit, if any, etc.) |  | 1 set
11.4 | 5% of each type of integral control units (if any), installed, mounted on actuator or installed separately and not less than two per type |  | 1 set
12. | VARIABLE SPEED DRIVES FOR (if applied)
12.1 | One complete drive per each type and rating installed |  | 1 set
12.2 | One of each type of drive converter transformer installed (if any) |  | 1 set
13. | LIGHTING AND POWER OUTLETS SYSTEM
13.1 | 5% of explosion proof lighting fixtures of any type installed in the Power Plant and not less than one per type |  | 1 set
13.2 | One of each type of photocell installed for lighting activation |  | 1 set
13.3 | 5% of aviation lighting fixtures and lamps of any type installed in the Power Plant and not less than two per type |  | 1 set
13.4 | One of each type of aviation lighting controllers, synchronization units and printed circuit boards (p.c.b.) installed |  | 1 set
14. | CATHODIC PROTECTION
14.1 | One of each type of rectoformer unit installed |  | 1 set
14.2 | 10% of the anodes of each type installed and not less than two per type |  | 1 set
14.3 | Complete test point box suitable for measuring the potential difference applied to the protected structures |  | 1 set
14.4 | One of each type of insulating joints including spark gaps installed |  | 1 set
15. | FIRE FIGHTING AND DETECTION SYSTEM
15.1 | 5% of any type of fire detectors together with the detector base and not less than one per type |  | 1 set
15.2 | 5% of each type of electronic I/O module and loop address module and not less than one per type |  | 1 set
15.3 | 10% of each type of p.c.b.s installed in the fire detection and firefighting panels and not less than one per type |  | 1 set
15.4 | 5% of each type of CO2 extinguishing local control boards and not less than one per type |  | 1 set
15.5 | 5% of each type of CO2 extinguishing system actuators and solenoid valves and not less than one per type |  | 1 set
15.6 | 10% of each type of deluge water system valves including solenoid valves and actuators and not less than one per type |  | 1 set
16. | PROTECTION DEVICES
16.1 | One complete protection relay for each type of protection relays installed for the Generators, Step-up transformers, 10÷15kV switchboards and Emergency Diesel Generator |  | 1 set
16.2 | One of each type of power supply units, DC/DC converters and suppression filters installed in the protection relays cubicles |  | 1 set
16.3 | One of each type of lock-out relay installed |  | 1 set
16.4 | One of each type of trip circuit supervision relays installed |  | 1 set
16.5 | 5% of each type of auxiliary relays with bases, installed at the protection cubicle and not less than two per type |  | 1 set
16.6 | 5% of each type of the fuses installed in the protection cubicle and not less than two per type |  | 1 set
15.7 | One of each type of test sockets installed at the protection panels |  | 1 set
TOTAL PRICE FOR THE ELECTRICAL SPARE PARTS
I & C and Station Utilities SPARE PARTS
1. | MEASUREMENTS
1.1 | Sensors, transmitters (binary and analog) and local instruments
1.1.1 | 10% but not less than two (2), for each type installed in the Project, with the exception of packaged units. |  | 1 set
1.1.2 | 10% but not less than one (1), for each type installed in the packaged units of the Project |  | 1 set
1.2 | Water analyzers
1.2.1 | 10% but not less than one (1) complete analyzer ready to operate, for each type installed in the Project |  | 1 set
1.2.2 | Consumables as probes, internal tubes, dosometric pumps, consumable part kits, filters, membranes and similar parts for two years operation of each analyzer according to the maker's manual maintenance requirements. |  | 1 set
1.3 | Gas analyzers
1.3.1 | One (1) complete analyzer ready to operate for each type installed in the Project (if applicable, such as Natural Gas, O2, NOx, CO, NH3 analyzers etc). |  | 1 set
1.3.2 | Consumables as filters, probes, cells and similar parts for two years operation of each analyzer according to the maker's manual maintenance requirements |  | 1 set
2. | LOCAL CONTROL BOXES
| Two (2) for each type of local |  | 1 set
boxes installed in the Project
3. | CLOSED LOOP ACTUATORS
3.1 | One (1) complete electrical actuator of each type installed in the Project (actuator is meant complete i.e. comprising motor, reduction gear, stroke mechanism etc.) |  | 1 set
3.2 | One (1) complete pneumatic actuator of each type installed in the Project (if applicable) |  | 1 set
4. | PCS (including the electronic part of the Gas Engine Genset governor and protection system)
4.1 | 10%, but not less than two (2) pieces, for each type of the electronic modules installed in the Project (i.e. controllers, I/O modules, communication modules, base plates, termination assemblies, etc.) |  | 1 set
4.2 | 10%, but not less than two (2) pieces, for each type of power supply units installed in the Project. |  | 1 set
4.3 | 10%, but not less than two (2) pieces for each type of auxiliary control equipment (MCB’s, auxiliary relays, fuses, indication LED’s, etc.) |  | 1 set
4.4 | One (1) piece for each type of network components (i.e. switches, optical link modules, converters, etc) |  | 1 set
5. | PACKAGE UNITS CONTROL SYSTEMS (in accordance with para 3.2 of Section B2}
5.1 | One (1) piece for each type of electronic modules (i.e. controllers, I/O modules, communication modules, base plates, termination assemblies, etc.) |  | 1 set
5.2 | One (1) piece for each type of power supply modules |  | 1 set
5.3 | 10%, but not less than two (2) pieces for each type of auxiliary control equipment (MCB’s, auxiliary relays, fuses, indication LED’s, etc.) |  | 1 set
6. | GAS ENGINE ELECTRONIC GOVERNOR (if not included in the PCS)
| One (1) complete GenSet Electronic Governor including controller, I/O modules, power supply modules, communication modules etc. |  | 1 set
7. | GAS ENGINE BACK-UP ELECTRONIC OVERSPEED SYSTEM
| One (1) complete Gas Engine back-up overspeed device |  | 1 set
8. | CLOSED LOOP CONTROL POWER UNITS
| 10%, but not less than two (2) pieces, for each type of power control units installed in the Project (including also the case of pneumatic actuators) |  | 1 set
9. | CONVENTIONAL INSTRUMENTATION
| One (1) for each type of indicators, recorders, push buttons etc. installed in the CCR, in the Gas Engines local control panels and package units local control panels. |  | 1 set
10. | OPERATOR STATION
10.1 | One (1) complete operator station with TFT monitor for the PCS ready to operate (including all the necessary software and licenses) |  | 1 set
10.3 | One (1) computer with licensed operating system and hardware identical to the PCS servers and operator station. |  | 1 set
11. | DISPLAY WALLS
11.1 | One (1) LCD display tile |  | 1 set
12. | TELEPHONE SYSTEM
12.1 | One (1) of each type of industrial telephone set installed |  | 1 set
13. | PUBLIC ADDRESS SYSTEM
13.1 | Set including all the p.c.bs., components as well as the power supply of the control unit of the system |  | 1 set
13.2 | 10% from each type of loudspeakers installed and not less than one |  | 1 set
13.3 | One (1) amplifier of each type installed |  | 1 set
13.4 | One (1)call station |  | 1 pc
13.5 | One (1) access panel |  | 1 pc
13.6 | Set of beacons of each type installed |  | 1 set
14 | CLOCK SYSTEM
14.1 | One (1) clock of each type installed |  | 1 set
15. | INTERGRATED SECURITY SYSTEM
15.1 | IP Colour (day/night) fixed type cameras |  | 2pcs
15.2 | Network PTZ Dome Colour camera |  | 1pc
15.3 | One of each type of fibber optic/copper transmitter and receiver installed. |  | 1 set
15.4 | One of each type of Ethernet switches installed |  | 1 set
15.5 | Heaters and blowers |  | 1 set
15.6 | One (1) of each type of panic push buttons installed |  | 1 set
15.7 | Interphone station |  | 1 pc
TOTAL PRICE FOR THE I&C SPARE PARTS
CHEMICAL PROCESSES SYSTEMS SPARE PARTS
1. | WATER TREATMENT SYSTEMS
1.1 | Desalination system
| RO membrane vessels |  | 1 pc
| RO membranes for one production line |  | 1 set
| For each valve, per nominal bore and nominal rating, not included in Section A, one complete valve |  | 1 set
Dosing pumps:
| - Diaphragms of each type & size installed |  | 2 sets
| - Packings of each type & size installed |  | 2 sets
| - Bearings of each type & size installed |  | 1 set
| - Gaskets of each type & size installed |  | 2 sets
| - Pump stroke regulation mechanism, one for each type installed |  | 1 set
| Pulsation dampeners of each type and size |  | 1 set
1.2 | Demineralization system
| For each valve, per nominal bore and nominal rating, not included in Section A, one complete valve |  | 1 set
| EDI module |  | 1 pc
| EDI Snubber circuit |  | 1 pc
| EDI Power controller |  | 1 pc
2. | WATER CHEMICAL CONDITIONING (DOSING) SYSTEM
| For each valve, per nominal bore and nominal rating, not included in Section A, one complete valve |  | 1 set
Dosing pumps:
| - Diaphragms of each type & size installed |  | 2 sets
| - Packings of each type & size installed |  | 2 sets
| - Bearings of each type & size installed |  | 1 set
| - Gaskets of each type & size installed |  | 2 sets
| - Pump stroke regulation mechanism, one for each type installed |  | 1 set
3. | SAMPLING SYSTEM
| For each valve, per nominal bore and nominal rating, not included in Section A, one complete valve |  | 1 set
| Standard service kit for the sampling system chillers |  | 2 sets
4. | WASTE WATER TREATMENT SYSTEM
| For each valve, per nominal bore and nominal rating, not included in Section A |  | 1 set
Dosing pumps:
| - Diaphragms of each type & size installed |  | 2 sets
| - Packings of each type & size installed |  | 2 sets
| - Bearings of each type & size installed |  | 1 set
| - Gaskets of each type & size installed |  | 2 sets
| - Pump stroke regulation mechanism, one for each type installed |  | 1 set
| Agitator complete with motor per each type installed |  | 1 set
5 | DeNOx SYSTEM (if applicable)
| For each valve, per nominal bore and nominal rating, not included in Section A, one complete valve |  | 2 sets
| Nozzles for all types & sizes installed |  | 2 sets
| Filter elements for each type |  | 2 sets
TOTAL PRICE FOR THE CHEMICAL PROCESSES SYSTEMS SPARE PARTS
TOTAL PRICE FOR THE SPARE PARTS